## ADC_Vac_Vbus_Ii
Vadc | 3.3 | V | ADC Ref. Voltage
Voltage is sensed using a resistor divider and Op-amp circuitry
Vbus
Ra | 3000000 | Ohms | R8+R11+R15
Rb | 11000 | Ohms | R16
Resitor Divider Gain | 0.0036533
Opamp Gain | 2
Vbus_max_sense | 451.65 | Volts
Vac
Rc | 3001000 | Ohms | R2+R5+R3+R60
Rd | 11000 | Ohms | R61, R55
Resitor Divider Gain | 0.0036654
Offset | 1.65 | Volts
Vac_max_sense | 450.15 | Volts
Current is sensed using a hall effect sensor LTSR-6-NP
Iinv
Vnominal | 0.625 | Volts | Nominal Range of Sensor in Volts
Inominal_rms | 3 | Irms | Nominal Range RMS Current
Inominal_max | 4.242 | Imax | Nominal Range Max Current
Re | 500000 | Ohms | R67
Rf | 330000 | Ohms | R68
Imax_sense | 16.968 | Amps

## SDFM_Vac_Vbus_Iout_Icf
Vsense_max | 0.3125 | Volts | AMC1304 SDFM Sensor Max Range
Rdiff | 12500 | Ohms | AMC1304 has fully differential Opamp, with 50Kohm feedback resistor and 12.5Kohm input resistorof R3 and 12.5Kohm
Vlinear_range | 0.25 | Volts
Voltage is sensed using a resistor divider circuitry
Vbus/ Vac
Rg | 4000000 | Ohms | R32+R37
Rh | 2400 | Ohms | R52
Reffective | 2013.4228 | Ohms | Second end of the modultaor is grounded the effective resistance is a parallel combination
Effective Reistor Divider Gain | 0.0005031
Vmax_sensed | 621.1458 | Volts
Vlinear_sensed | 496.9167 | Volts
Current is sensed using a shunt resistor
Iout, If
Rsh | 0.02 | Ohms
Imax_sensed | 15.625 | Amps
Ilinear_sensed | 12.5

## UPS Li & Cf Sel
Power Rating | 600 | VA
Switching Frequency | 20000 | Hz
Current at 110Vrms | 5.4545 | Irms | 7.7127 | Ipeak | 1.5425 | delta I
Current at 220Vrms | 2.7273 | Irms | 3.8564 | Ipeak | 1.5425 | delta I
DC Bus | 380 | V
Inductance Li Calculation
Ripple Toerable at 110 | 20 | percent
Li (min) | 0.0030793 | H
Ripple Tolerable at 220 | 40 | percent
Li (min) | 0.0030793 | H
Capacitance Li Calculation
Cf | 20 | uF
LC Filter Cuttoff | 641.649 | Hz

## Grid Conn. Li, Cf, Lg Sel
Power Rating | 600 | VA
Switching Frequency | 20000 | Hz
Current at 110Vrms | 5.4545 | Irms | 7.7127 | Ipeak | 1.5425 | delta I
Current at 220Vrms | 2.7273 | Irms | 3.8564 | Ipeak | 1.5425 | delta I
DC Bus | 380 | V
f at 110 | 60 | Hz
f at 220 | 50 | Hz
Inductance Li Calculation
Ripple Toerable at 110 | 20 | percent
Li (min) at | 0.0030793 | H
Ripple Tolerable at 220 | 40 | percent
Li (min) | 0.0030793 | H
Capacitance Cf Calculation
VAR at 110 | 0.76 | percent
Cf at 110Vrms for rated VAR exchange in CAP | 1.0002 | uF
VAR at 220 | 2.6 | percent
Cf at 110Vrms for rated VAR exchange in CAP | 1.0265 | uF
LC Filter Cuttoff | 2869.3151 | Hz
Inductance Lg Calculation
Fsw/6 | 3333.3333 | uF
Lg | 0.00094 | H
LCL Filter Resonance | 5933.2265 | Hz
DC Bus Calculation
% DC Bus Ripple Tolerable | 5 | percent
DC Bus Ripple | 19 | V
Minimum Bus Voltage (V) | 361 | V
Cbus at 110 Vrms | 177.5694 | uF
Cbus at 220 Vrms | 213.0833 | uF
Switching Ripple Attenuation
RAFsw | 0.067426
RAFsw in dB | -23.4235
Inverter current sw attenuation (factor of the ripple tolerated in the inductor) at 110Vrms | -13.9794
Inverter current sw attenuation (factor of the ripple tolerated in the inductor) at 220Vrms | -7.9588
Total Switching Ripple at 110Vrms | -37.4029
Total Switching Ripple at 220Vrms | -31.3823

## Li Design
Inductance Specification
Desired Inductance Value | 3 | mH
DC Current | 5 | Amps | Faraday's Law
Ripple | 20 | %
Delta I | 1.414 | Amps
Vdc_Bus | 380 | V | Ampere's Law
Max energy stored in the inductor | 2.9991 | W
Wire Selection
Wire Gauge | 18 | AWG
Diameter Complete of the | 1.07 | mm
Cross Section Area | 0.89875 | mm^2
Conductor resistance | 22.4 | Ohm/Km
Core Specification
Core | C055439A2 | http://www.mag-inc.com/
Permeance of the core | 135 | nH/N^2
Window Area of the core selected | 427 | mm^2
Inductor Design Check & Specification
Winding Factor | 0.6
Max. No of Turns Possible | 285.0637
N: Turns Required for the desired inductance , must be less than the Max. No of Turns allowed with the core selection | 149.0712
Winding Factor | 31.3764 | %
Winding Length for Winding Factor percentage for the core selected | 68.2 | mm
Length of wire needed for N Turns | 10166.6557 | mm
Resistance (DCR) | 0.22773 | Ohms
Current Density (J) | 5.5633 | A/mm^2

## SPLL Calculations
SPLL Specification
For tuning of the SPLL, the PLL is assumed to be a second order system and the settling time and damping ratio equation of a second order system are used to tune the loop
Simplified PLL TF is given as
Compare this with generic second order equation
Where
Analog Coefficients
First get the values for natural frequency from an assumption of setlling time
Setlling Time | ts | 0.04 | ms
Damping Ratio |  | 0.7
Error Band |  | 0.05
c=wn/wd |  | 1.4003
ln(c/delta) |  | 3.3324
83.3101
wn |  | 119.0144
Substituting we get Kp and Ki
Ti |  | 0.011763
Kp |  | 166.6202
Ki |  | 14164.4389
Digital Coefficients
Comparing this with digital implementation of PI controller
Assuming vgrid=1
Fs |  | 10000 | Hz
Ts |  | 0.0001
B0 |  | 167.3284
B1 |  | -165.912